## Single VFD (hidden)
2010 AccuSine Selection Research |  |  |  | 2010-02-10
HarmCalc for specific VFD and VFD combinations
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61 |  |  | AVERAGES
SCR = | 2614.811 | SCR = | 2704.9769 |  | SCR = | 3099.5455 | SCR = | 2565.986 | SCR = | 2603.9612 | SCR = | 2825.1865 | SCR = | 2548.2383 | SCR = | 2546.6871 |  | SCR = 2500
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 185.2% | 0% | 184.3% |  | 0% |  | 0% | [9 empty] | 0% | 184.8%
[5 empty] | 1.35% | 59.42% | 0.96% | 66.97% | 1.06% | 64.77% | [6 empty] | 1.123% | 63.72%
1.5% | 51.24% | 1.5% | 52.22% |  | 1.5% |  | 1.5% | [9 empty] | 1.5% | 51.73%
[5 empty] | 2.85% | 37.6% | 2.46% | 41.01% | 2.56% | 40.21% | 2.96% | 34.79% |  |  | 2.24% | 43.19% | 2.614% | 39.36%
3% | 33.27% | 3% | 34.02% |  | 3% |  | 3% | [5 empty] | 3.26% | 34.62% |  |  | 3.087% | 33.97%
[5 empty] | 4.35% | 27.31% | 3.96% | 29.31% | 4.06% | 28.92% | 4.46% | 26.07% | 4.76% | 25.96% | 3.74% | 30.58% | 4.222% | 28.03%
5% | 22.72% | 5% | 23.27% |  | 5% |  | 5% | [9 empty] | 5% | 22.99%
[5 empty] | 6.35% | 20.1% | 5.96% | 21.31% | 6.06% | 21.11% | 5.96% | 20.9% | 6.26% | 20.83% | 5.24% | 23.72% | 5.972% | 21.33%
7.5% | 16.3% | 7.5% | 16.73% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 18.33% | 7.413% | 17.12%
[5 empty] | 8.85% | 15.25% | 8.46% | 15.97% | 8.56% | 15.88% | 7.96% | 16.62% | 8.26% | 16.59% |  |  | 8.418% | 16.06%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61 |  |  | AVERAGES
SCR = | 1012.1849 | SCR = | 1020.9674 |  | SCR = | 1005.4122 | SCR = | 940.8615 | SCR = | 972.1455 | SCR = | 968.6354 | SCR = | 1019.2953 | SCR = | 990.3783 |  | SCR = 1000
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 132.7% | 0% | 145.5% |  | 0% |  | 0% | [10 empty] | 139.1%
[5 empty] | 1.35% | 57.86% | 0.96% | 65.64% | 1.06% | 63.56% | [7 empty] | 62.35%
1.5% | 50.19% | 1.5% | 51.56% |  | 1.5% |  | 1.5% | [10 empty] | 50.88%
[5 empty] | 2.85% | 36.86% | 2.46% | 40.43% | 2.56% | 39.7% | 2.96% | 36.65% |  |  | 2.24% | 42.56% |  | 39.24%
3% | 32.81% | 3% | 33.74% |  | 3% |  | 3% | [5 empty] | 3.26% | 34.21% |  |  |  | 33.59%
[5 empty] | 4.35% | 26.92% | 3.96% | 29.03% | 4.06% | 28.64% | 4.46% | 27.12% | 4.76% | 25.72% | 3.74% | 30.26% |  | 27.95%
5% | 22.49% | 5% | 23.14% |  | 5% |  | 5% | [10 empty] | 22.81%
[5 empty] | 6.35% | 19.89% | 5.96% | 21.15% | 6.06% | 20.96% | 5.96% | 21.58% | 6.26% | 20.66% | 5.24% | 23.53% |  | 21.3%
7.5% | 16.19% | 7.5% | 16.66% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 18.22% |  | 17.02%
[5 empty] | 8.85% | 15.14% | 8.46% | 15.88% | 8.56% | 15.8% | 7.96% | 17.05% | 8.26% | 16.49% |  |  |  | 16.07%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61 |  |  | AVERAGES
SCR = | 486.4765 | SCR = | 510.4837 |  | SCR = | 473.1352 | SCR = | 484.6862 | SCR = | 503.4325 | SCR = | 484.3177 | SCR = | 509.6477 | SCR = | 509.3374 |  | SCR = 500
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 121.1% | 0% | 125.3% |  | 0% |  | 0% | [10 empty] | 123.2%
[5 empty] | 1.35% | 56.3% | 0.96% | 63.73% | 1.06% | 61.84% | [7 empty] | 60.62%
1.5% | 49.52% | 1.5% | 50.7% |  | 1.5% |  | 1.5% | [10 empty] | 50.11%
[5 empty] | 2.85% | 36.19% | 2.46% | 39.64% | 2.56% | 38.93% | 2.96% | 35.87% |  |  | 2.24% | 41.6% |  | 38.45%
3% | 32.52% | 3% | 33.35% |  | 3% |  | 3% | [5 empty] | 3.26% | 33.54% |  |  |  | 33.14%
[5 empty] | 4.35% | 26.54% | 3.96% | 28.6% | 4.06% | 28.24% | 4.46% | 26.67% | 4.76% | 25.35% | 3.74% | 29.76% |  | 27.53%
5% | 22.35% | 5% | 22.96% |  | 5% |  | 5% | [10 empty] | 22.66%
[5 empty] | 6.35% | 19.67% | 5.96% | 20.92% | 6.06% | 20.75% | 5.96% | 21.3% | 6.26% | 20.42% | 5.24% | 23.22% |  | 21.05%
7.5% | 16.12% | 7.5% | 16.56% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 18.04% |  | 16.91%
[5 empty] | 8.85% | 15.02% | 8.46% | 15.75% | 8.56% | 15.67% | 7.96% | 16.87% | 8.26% | 16.33% |  |  |  | 15.93%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61
SCR = | 261.4811 | SCR = | 270.4977 |  | SCR = | 309.9545 | SCR = | 256.5986 | SCR = | 260.3961 | SCR = | 282.5186 | SCR = | 254.8238 | SCR = | 254.6687 |  | SCR = 250
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 113.2% | 0% | 114% |  | 0% |  | 0% | [10 empty] | 113.6%
[5 empty] | 1.35% | 53.85% | 0.96% | 60.49% | 1.06% | 58.74% | [7 empty] | 57.69%
1.5% | 48.91% | 1.5% | 49.83% |  | 1.5% |  | 1.5% | [10 empty] | 49.37%
[5 empty] | 2.85% | 35.05% | 2.46% | 38.24% | 2.56% | 37.55% | 2.96% | 34.79% |  |  | 2.24% | 39.76% |  | 37.08%
3% | 34.24% | 3% | 32.98% |  | 3% |  | 3% | [5 empty] | 3.26% | 32.27% |  |  |  | 33.16%
[5 empty] | 4.35% | 25.93% | 3.96% | 27.87% | 4.06% | 27.5% | 4.46% | 26.07% | 4.76% | 24.59% | 3.74% | 28.8% |  | 26.79%
5% | 22.22% | 5% | 22.78% |  | 5% |  | 5% | [10 empty] | 22.5%
[5 empty] | 6.35% | 19.34% | 5.96% | 20.53% | 6.06% | 20.34% | 5.96% | 20.9% | 6.26% | 19.94% | 5.24% | 22.63% |  | 20.61%
7.5% | 16.05% | 7.5% | 16.47% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 17.67% |  | 16.73%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61
SCR = | 183.0368 | SCR = | 182.8539 |  | SCR = | 168.8956 | SCR = | 179.2757 | SCR = | 164.2097 | SCR = | 163.9316 | SCR = | 167.8105 | SCR = | 173.305 |  | SCR = 150
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 92.92% | 0% | 90.88% |  | 0% |  | 0% | [10 empty] | 91.9%
[5 empty] | 1.35% | 50.54% | 0.96% | 57.33% | 1.06% | 54.82% | [7 empty] | 54.23%
1.5% | 46.18% | 1.5% | 46.53% |  | 1.5% |  | 1.5% | [10 empty] | 46.36%
[5 empty] | 2.85% | 33.52% | 2.46% | 36.85% | 2.56% | 35.78% | 2.96% | 32.99% |  |  | 2.24% | 38.06% |  | 35.44%
3% | 31.02% | 3% | 31.48% |  | 3% |  | 3% | [5 empty] | 3.26% | 31% |  |  |  | 31.17%
[5 empty] | 4.35% | 25.09% | 3.96% | 27.11% | 4.06% | 26.54% | 4.46% | 25.04% | 4.76% | 23.84% | 3.74% | 27.88% |  | 25.92%
5% | 21.62% | 5% | 22.03% |  | 5% |  | 5% | [10 empty] | 21.82%
[5 empty] | 6.35% | 18.86% | 5.96% | 20.1% | 6.06% | 19.8% | 5.96% | 20.24% | 6.26% | 19.44% | 5.24% | 22.05% |  | 20.08%
7.5% | 15.72% | 7.5% | 16.06% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 17.33% |  | 16.37%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61
SCR = | 102.6854 | SCR = | 107.2743 |  | SCR = | 94.0862 | SCR = | 107.4317 | SCR = | 111.6248 | SCR = | 111.3344 | SCR = | 103.8912 | SCR = | 102.2952 |  | SCR = 100
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 74.92% | 0% | 75.81% |  | 0% |  | 0% | [10 empty] | 75.36%
[5 empty] | 1.35% | 44.51% | 0.96% | 51.43% | 1.06% | 50.51% | [7 empty] | 48.82%
1.5% | 41.8% | 1.5% | 42.67% |  | 1.5% |  | 1.5% | [10 empty] | 42.23%
[5 empty] | 2.85% | 30.65% | 2.46% | 34.18% | 2.56% | 33.81% | 2.96% | 31.16% |  |  | 2.24% | 34.86% |  | 32.93%
3% | 28.96% | 3% | 29.63% |  | 3% |  | 3% | [5 empty] | 3.26% | 28.94% |  |  |  | 29.18%
[5 empty] | 4.35% | 23.42% | 3.96% | 25.63% | 4.06% | 25.42% | 4.46% | 23.97% | 4.76% | 22.6% | 3.74% | 26.1% |  | 24.52%
5% | 20.56% | 5% | 21.09% |  | 5% |  | 5% | [10 empty] | 20.82%
[5 empty] | 6.35% | 17.19% | 5.96% | 19.26% | 6.06% | 19.16% | 5.96% | 19.54% | 6.26% | 18.61% | 5.24% | 20.92% |  | 19.11%
7.5% | 15.16% | 7.5% | 15.56% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 16.62% |  | 15.78%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61
SCR = | 49.8758 | SCR = | 53.6371 |  | SCR = | 47.0431 | SCR = | 53.7159 | SCR = | 55.8124 | SCR = | 55.6672 | SCR = | 51.9456 | SCR = | 51.1476 |  | SCR = 50
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 55.41% | 0% | 57.2% |  | 0% |  | 0% | [10 empty] | 56.31%
[5 empty] | 1.35% | 34.98% | 0.96% | 40.88% | 1.06% | 40.54% | [7 empty] | 38.8%
1.5% | 34.75% | 1.5% | 35.88% |  | 1.5% |  | 1.5% | [10 empty] | 35.31%
[5 empty] | 2.85% | 25.74% | 2.46% | 29.09% | 2.56% | 28.92% | 2.96% | 26.61% |  |  | 2.24% | 28.91% |  | 27.85%
3% | 25.33% | 3% | 26.14% |  | 3% |  | 3% | [5 empty] | 3.26% | 24.66% |  |  |  | 25.38%
[5 empty] | 4.35% | 20.43% | 3.96% | 22.62% | 4.06% | 22.54% | 4.46% | 21.18% | 4.76% | 19.9% | 3.74% | 22.6% |  | 21.55%
5% | 18.62% | 5% | 19.22% |  | 5% |  | 5% | [10 empty] | 18.92%
[5 empty] | 6.35% | 16.12% | 5.96% | 17.49% | 6.06% | 17.46% | 5.96% | 12.89% | 6.26% | 16.76% | 5.24% | 18.6% |  | 16.55%
7.5% | 14.11% | 7.5% | 14.53% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 15.15% |  | 14.6%
5HP ATV61 |  | 10HP ATV61 |  |  | 30HP ATV61 |  | 60HP ATV 61 |  | 100HP ATV 61 |  | 250HP ATV61 |  | 400HP ATV61 |  | 700HP ATV61
SCR = | 19.8708 | SCR = | 20.805 |  | SCR = | 18.8172 | SCR = | 20.4548 | SCR = | 22.6524 | SCR = | 19.2494 | SCR = | 20.7782 | SCR = | 21.4341 |  | SCR = 20
Installed Z% | TDD | Installed Z% | TDD |  | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD | Installed Z% | TDD
0% | 26.11% | 0% | 26.77% |  | 0% |  | 0%
[5 empty] | 1.35% | 20.95% | 0.96% | 22.39% | 1.06% | 22.16% | [7 empty] | 21.83%
1.5% | 20.22% | 1.5% | 20.77% |  | 1.5% |  | 1.5% | [10 empty] | 20.5%
[5 empty] | 2.85% | 17.23% | 2.46% | 18.24% | 2.56% | 18.1% | 2.96% | 16.59% |  |  | 2.24% | 18.95% |  | 17.82%
3% | 16.52% | 3% | 16.98% |  | 3% |  | 3% | [5 empty] | 3.26% | 16.95% |  |  |  | 16.82%
[5 empty] | 4.35% | 14.7% | 3.96% | 15.44% | 4.06% | 15.36% | 4.46% | 14.34% | 4.76% | 14.61% | 3.74% | 16.01% |  | 15.08%
5% | 13.4% | 5% | 13.76% |  | 5% |  | 5% | [10 empty] | 13.58%
[5 empty] | 6.35% | 12.48% | 5.96% | 12.96% | 6.06% | 12.93% | 5.96% | 12.75% | 6.26% | 12.96% | 5.24% | 13.95% |  | 13%
7.5% | 11.22% | 7.5% | 11.46% |  | 7.5% |  | 7.5% | [7 empty] | 7.24% | 12.1% |  | 11.59%

## work page (hidden)
5000
[6 empty] | source SC MVA | SCA at Utility or GEN @ PCC Volt |  |  | #DIV/0!
|  | SCA | voltage |  | SC MVA |  |  | Equiv at connected V |  |  |  | IEEE 519-1992 Table 10.3
TDD SHCR | Utility SCA | 0 | 0 |  | 0 | 0 | 0 | 0 | 0 |  |  | Isc/Iload |  | TDD
2501 | Generator SCA | 0 | 0 |  | 0 | 0 |  | 0 |  |  |  | < 20 | 20 | 5%
| Dist SCA | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 |  | 20<50 | 50 | 8%
| Other SCA | 0 | 0 |  | 0 | 0 |  | 0 | 0 | 0 | 0 | 50<100 | 100 | 12%
[11 empty] | 0 | 100<1000 | 1000 | 15%
| PCC SCA | 0 | 480 | [7 empty] | 0 | >1000 | 5000 | 20%
| SCA SYSTEM | 0 | util or gen
[12 empty] | IEEE519-1992 req'd |  | 0.2
|  | Measure | Equipment | DPF | [7 empty] | G5/4-1 @ 10 MVA |  |  | GBT
|  | KW | PWM VFD | 0.95 | [6 empty] | TDD | 8% |  | TDD | 12%
|  | HP | VSI VFD | -0.05 | [6 empty] | TDD req'd | 0% |  | TDD req'd | 0%
|  | KVA | AFE VFD | 1
|  |  | DC drive | -0.05
|  |  | DC power supply - Inductive | -0.05 | [7 empty] | PCC
|  |  | DC power supply - Resistive | -0.05 | [7 empty] | Utility | [5 empty] | Distribution Transformer - Secondary | no
|  |  | UPS w/Diode rectifier | 0.95 | [7 empty] | Generator | [5 empty] | Generator | no
|  |  | UPS w/SCR rectifier | -0.05 | [7 empty] | Distribution Transformer - Secondary | [5 empty] | MCC Transfomer - Secondary | no
|  |  | UPS w/AFE rectifier | 1 | [7 empty] | MCC Transfomer - Secondary | [5 empty] | Utility | no
|  |  | UV power supply | 1
|  |  | Electronic lighting ballasts - std | 0.975 |  |  |  |  | SCR
|  |  | Electronic lighting ballasts - Premium | 1 | [5 empty] | Short Circuit Ratio
[9 empty] | Installed Z% | 20 | 50 | 100 | 150 | 250 | 500 | 1000 | 2500
[9 empty] | 0% | 26.44% | 56.31% | 75.36% | 91.9% | 113.6% | 123.2% | 139.1% | 184.8%
[9 empty] | 1.15% | 21.83% | 38.8% | 48.82% | 54.23% | 57.69% | 60.62% | 62.35% | 63.72%
[8 empty] | Capacitive | 1.5% | 20.5% | 35.31% | 42.23% | 46.36% | 49.37% | 50.11% | 50.88% | 51.73%
[8 empty] | resistive | 2.5% | 17.82% | 27.85% | 32.93% | 35.44% | 37.08% | 38.45% | 39.24% | 39.36%
[9 empty] | 3% | 16.82% | 25.38% | 29.18% | 31.17% | 33.16% | 33.14% | 33.59% | 33.97%
[9 empty] | 4.25% | 15.08% | 21.55% | 24.52% | 25.92% | 26.79% | 27.53% | 27.95% | 28.03%
[8 empty] | Inductive | 5% | 13.58% | 18.92% | 20.82% | 21.82% | 22.5% | 22.66% | 22.81% | 22.99%
[9 empty] | 6% | 13% | 16.55% | 19.11% | 20.08% | 20.61% | 21.05% | 21.3% | 21.33%
[9 empty] | 7.5% | 11.59% | 14.6% | 15.78% | 16.37% | 16.73% | 16.91% | 17.02% | 17.12%
Standard Applied
IEEE 519-1992
Installed Impedance
none
1.5%
3%
5%
7.5%
default

## Selection Basics (hidden)
PWM VFD (Defaults) | According to HarmCalc | [6 empty] | weighted Z% | SCR
Drive HP | Z% | [7 empty] | 20 | 50 | 100 | 200 | 250 | 500 | 1000 | 2500
1 | 0 | [5 empty] | 1x20+1x25 | 1.0439 | 23.96% | 45.94 | 60.24 | 67.87 |  | 81.01 | 84.74 | 88.44 | HarmCalc
2 | 0 | [7 empty] | 23.6% | 45.08% | 58.74% | 68.88% | 81.2% | 87.65% | 97.7% | 116.2% | Weighted avg of each
3 | 0
5 | 0 | [5 empty] | 1x100+1x400 | 2.567 | 17.3 | 25.39 | 30.3 | 33.56 | 34.21 | 35.6 | 37.62 | 37.93
7.5 | 0 | [7 empty] | 18.08% | 28.11% | 33.63% | 36.18% | 38.02% | 39.69% | 40.59% | 41.17%
10 | 0
15 | 0 | [5 empty] | 2x75+1x500 | 2.8405 | 17.59 | 27.2 | 32.76 | 36.55 | 37.4 | 39.19 | 40.13 | 40.78
20 | 0 | [7 empty] | 18.34% | 28.89% | 34.69% | 37.35% | 39.33% | 41.09% | 42.04% | 42.66%
25 | 0.6769
30 | 1.3497
40 | 1.3582
50 | 1.2048
60 | 0.9555
75 | 1.1838
100 | 1.0557
125 | 2.2825
150 | 1.7207
175 | 2.5836
200 | 2.9621 | [11 empty] | Qty | Size | Equivalent Z calculation |  | sumproduct qty/size | [5 empty] | PWM VFD Z |  | PWM VFD DPF
250 | 2.703 | [6 empty] | 1.15% |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
300 | 3.2635 | [6 empty] | 250 |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
350 | 3.1549 | [6 empty] | 57.69% |  |  |  |  | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
400 | 2.9389 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
450 | 2.646 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
500 | 3.2378 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
550 | 2.9731 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
600 | 3.3278 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
700 | 2.24 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
900 | 2.6461 | [11 empty] | 0 | 0 | 0 |  | 0 | 0 |  | 0 |  |  | 0
[14 empty] | Weighted AVG | 0 |  | 0 | 0 |  | 0
[14 empty] | Adjusted multiplier | 3
PWM VFD
| Short Circuit Ratio | [9 empty] | Apply AccuSine selection mulitplier according to equivalent impedance of loads installed.
Installed Z% | 20 | 50 | 100 | 150 | 250 | 500 | 1000 | 2500 |  |  | % Impedance | Multiplier |  |  | 0 | [6 empty] | 0
0% | 26.44% | 56.31% | 75.36% | 91.9% | 113.6% | 123.2% | 139.1% | 184.8% |  |  | 0 | 3 | not possible to predict discontinued orders |  |  |  |  | 3 | 0 |  | 3 | 1.5
1.15% | 21.83% | 38.8% | 48.82% | 54.23% | 57.69% | 60.62% | 62.35% | 63.72% |  |  | 1.5 | 1.6 | Some high orders will be discontinued |  |  |  |  | 1.6 | 1.5 |  | 1.6 | 3
1.5% | 20.5% | 35.31% | 42.23% | 46.36% | 49.37% | 50.11% | 50.88% | 51.73% |  |  | 3 | 1.2 | [5 empty] | 1.2 | 3 |  | 1.2 | 5
2.5% | 17.82% | 27.85% | 32.93% | 35.44% | 37.08% | 38.45% | 39.24% | 39.36% |  |  | 5 | 1.1 | [5 empty] | 1.1 | 5 |  | 1.1 | 7.5
3% | 16.82% | 25.38% | 29.18% | 31.17% | 33.16% | 33.14% | 33.59% | 33.97% |  |  | 7.5 | 1 | [5 empty] | 1 | 7.5 |  | 1 | 7.5
4.25% | 15.08% | 21.55% | 24.52% | 25.92% | 26.79% | 27.53% | 27.95% | 28.03%
5% | 13.58% | 18.92% | 20.82% | 21.82% | 22.5% | 22.66% | 22.81% | 22.99% |  |  | 3 | 0 | 1.5 | 3 |  |  |  | 1 | 7.5 |  | 1 | 7.5
6% | 13% | 16.55% | 19.11% | 20.08% | 20.61% | 21.05% | 21.3% | 21.33% |  |  |  | 3 | 1.6 |  |  |  |  | 1.1 | 5 |  | 1.1 | 7.5
7.5% | 11.59% | 14.6% | 15.78% | 16.37% | 16.73% | 16.91% | 17.02% | 17.12% | [9 empty] | 1.2 | 3 |  | 1.2 | 5
[18 empty] | 1.6 | 1.5 |  | 1.6 | 3
[18 empty] | 3 | 0 |  | 3 | 1.5
2500
Other types of Converters | [11 empty] | ShCR = | 2501 | #DIV/0! |  | Q |  |  | T
Converter type | Equivalent Z% | [10 empty] | %z | TDD |  | z higher | TDD higher |  | z lower | tdd low |  | delta tdd | delta z | delta zset | Adj TDD | 12-p adj
12-P | 5% | Assume THDi = 10% | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
!8-P | 5% | Assume THDi = 5% | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
VVI VFD | 5% | Assume DC bus has 3% Z for harmonic current; if no LR installed notches will be large for THDv | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
AFE VFD | n/a | TDD = 5% | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
DC Drives | 5% | Assume DC bus has 3% Z for harmonic current; if no LR installed notches will be large for THDv | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
UPS diode | 5% | [10 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
UPS SCR | 5% | Assume DC bus has 3% Z for harmonic current; if no LR installed notches will be large for THDv | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
UPS IGBT | n/a | TDD = 5% | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
SCR inductive | 5% | Assume DC bus has 3% Z for harmonic current; if no LR installed notches will be large for THDv | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
SCR resistive | 0% | SCR type with 3% line reactor | [9 empty] | 0 | 0% |  | 0 | 184.8% |  | 0 | 0% |  | -1.8476 | 0 | 0 | 0% | 0%
SCR capacitive | 0% | SCR type with 3% line reactor
UV Ballast - Normal | 3% | Transformer input
UV Ballast - Premium | 3% | TDD = 5%
Ozone Generator | 3% | SCR type with 3% line reactor | [9 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
Notes: | [11 empty] | 0 | 0 | 0
Best Practice: use => 3% line reactors | [11 empty] | 0 | 0 | 0
| VFD: lower TDD | [10 empty] | 0 | 0 | 0
| SCR: Smooth voltage notch | [10 empty] | 0 | 0 | 0
| Best performance | [10 empty] | 0 | 0 | 0
| Smallest size AHF | [10 empty] | 0 | 0 | 0
[12 empty] | 0 | 0 | 0
If VFD has no impedance = can't perdict TDD levels (AHF turns off harmonic orders to keep AHF on line)

## Instructions
AccuSine PCS+ and AccuSine PFV+ Selection Tool
|  |  | Release Date: | Release Date: | 2017-05-22
Not applicable for neutral harmonic current calculations.
Not applicable for VAR Compensation (Flicker) selection.
Not applicable for Mains Current Balancing selection.
Not applicable for calculating leading to lagging or lagging to leading PF correction.
1. | This selection tool is applicable for selecting an optimized AccuSine PCS+ or PFV+ system to be used for any combination of the following modes: harmonic mitigation, displacement power factor correction (Cos ɸ), or both.
2. | Follow the 'Comments' and 'Pop-up Statements' that appear. They are included as operator directions to provide ease of use.
| a. | Complete the 'Electrical System 1-line' worksheet when compliance to a harmonic standard is required or when AccuSine+ connection voltage is other than 480 VAC.
| b. | No electrical system information is required when selection is made for a specified harmonic current distortion (THDi) value in the 'THDi Required' cell or when harmonic mode is not selected. [A default Short Circuit Ratio (ShCR) of 2501:1 is used if no electrical system data is entered.]
| c. | Default AccuSine+ System connection voltage is 480 VAC. To modify, go to 'Electrical System 1-line' worksheet. Enter the desired VAC of connection at the 'MCC Transformer' data entry location.
| d. | Cell comments and pop-up statements are provided for clarifications and directions.
| e. | All yellow cells are data entry fields.
| f. | Complete the "AccuSine Sizing Tool' worksheet to define nonlinear loads and linear loads for AccuSine PCS+ or AccuSine PFV+ selection.
| g. | An 'User Selected AccuSine Rating @ unit base voltage' must be entered on the 'AccuSine Sizing Tool' worksheet to provide a completed results summary. Enter a rating that is rounded up to the nearest integer for optimum selction.
3. | The "Server" worksheet provides a selection for leading displacement power factor (DPF) correction. It is assumed that the server utilizes switched mode power supplies (SMPS) defined as buck-boost converters with less than 5% THD(i) at all operating load levels. Since the DPF is leadng all DPF values are negative. Selection is for AccuSine PFV+ only.
| a. | The 'User Selected AccuSine rating @ unit base voltage' must be entered to complete the selection. Enter a rating that is rounded up the nearest integer for optimum selection.
4. | AccuSine PCS+ has the ability to assign functional priority between Harmonic mode and PF Correction mode. Adjustment of priority can optimize (may reduce) the size of the AccuSine PCS+ systems. "Percent of AccuSine PCS+ system assigned for Harmonic Mitigation" must be completed and adjusted to optimize the AccuSine PCS+ System selection when multiple modes are selected with Harmonic mode. This assignment is on the 'AccuSine Sizing Tool' worksheet.
| a. | If it is desired that Harmonic mode has first priority, enter 100% in 'Percent of AccuSine PCS+ system assigned for Harmonic Mitigation' cell. After harmonic correction, the remaining capacity is used for reactive current injection (PF Correction). If all of the capacity is used for harmonic correction, then no PF correction can occur.
| b. | If it is desired that PF mode have first priority, enter 0% in 'Percent of AccuSine PCS+ system assigned for Harmonic Mitigation' cell. This assigns the full capacity of the AccuSine PCS+ system to first perform PF correction, then use the remaining capacity to perform Harmonic correction. If all of the capacity is used for PF correction and/or Mains Current Balancing, then no Harmonic mitigation can occur.
| c. | By assigning values between 0% and 100%, the allocation of the AccuSine PCS+ system can be adjusted. Proper adjustment will optimize the AccuSine PCS+ system size.
5. | The worksheet titled 'Model Selector' uses information from the 'AccuSine Selection Tool' or "Server' worksheet to identify the quantities and model numbers for the AccuSine system that meet your needs. Selection of enclosure style is required on this worksheet to complete model selection. Adjustment for ambient temperature and altitude are included to account for unit derating.
6. | The worksheet titled 'CT Selector' uses data from 'AccuSine Selection Tool' or "Server" and 'Model Selector' worksheets to identify the CT size and quantities required. Additional data entry is required to complete.
7. | The worksheet titled 'Typical THDi Levels' displays typical Total THDi at full load values for PWM VFD with different amounts of installed inductive impedance (line reactors or DC bus chokes) at various short circuit current values. DC bus chokes and input line reactor impedances (Z%) are summed for total impedance for PWM VFD. The results are used for PWM VFD solutions. BEST PRACTICE for 6-pulse PWM VFD is inclusion of 3% to 5% total impedance either installed in the DC bus, on the 3-phase mains input, or both for significant initial THDi reductions. If very low to no impedance is installed compliance to any standard is doubtful.
8. | DC drives, UPS w/SCR (thyristor) rectifiers, and SCR (thyristor) power supplies cause a unique phenomena identified as 'voltage notching'. Voltage notching can adversely effect other SCR (thyristor) rectifiers and electronic loads installed on the same distribution bus. Voltage notching can only be reduced by installing line reactors rated from 3% to 7.5%. High source impedance (such as back up generators) requires higher load impedance. Active harmonic filters cannot remedy voltage notching due to SCR (thyristor) rectifiers. Input line reactors are required. BEST PRACTICE is to install 3-phase line reactors with 3-7.5% impedance at the input rectifier to smooth voltage notches and reduce voltage distortion due to the voltage notches.
If there are any questions, please, consult your local Schneider Electric representative.
AccuSine® is a registered trademark of Schneider Electric

## Electrical System 1-line
AccuSine+® Electrical Network Selection
Date:
Customer Name:
Project ID: |  |  |  |  | Project Name: | [5 empty] | x
Address:
City, State (Province):
Postal Code | [5 empty] | Country:
Prepared by:
Electrical System Single-Line Diagram
Mains Selected:
| Utility Select | [6 empty] | Generator Select
| Voltage |  | V |  |  |  |  | KW |  | kW
| ShCA |  | A |  |  |  |  | Voltage |  | V
[8 empty] | Subtransient Reactance |  | X"d
|  |  |  | Transfer Switch |  |  |  | PF rating (Cos ɸ)
Distribution Transformer
| KVA |  |  | kVA |  | Selected PCC: |  | Utility
| Secondary Voltage |  |  | V
| Impedance |  |  | Z
Distribution Bus
MCC Transformer
[5 empty] | KVA |  |  | kVA
[5 empty] | Secondary Voltage |  |  | V
[5 empty] | Impedance |  |  | Z
AccuSine System Connection Voltage
[5 empty] | MCC Bus |  | 480 | VAC
Linear and Nonlinear Loads
AccuSine® is a registered trademark of Schneider Electric
Note on J40: mpl649: The voltage of connection for the AccuSine system is the voltage listed here. Default is 480 VAC.

## AccuSine Sizing Tool
Selection of AccuSine+® Rating | [10 empty] | The PCC selected does not exist! Enter Electrical System Data for the selected PCC on the 'Electrical System 1-line' worksheet! | [10 empty] | x | IEEE 519-2014
Customer Name: | [7 empty] | Date:
Project ID: | [5 empty] | Project Name:
There is no installed inductance (Z). Therefore, compliance to any standard cannot be achieved!
The installed inductance (Z) is very low. Compliance to any standard is doubtful!
'Utility' has been selected as source. Data entry of 'Voltage' and 'Short Circuit Amperes' is required!
'Utility' has been selected as the PCC. Entry of 'Utility' parameters is required! 'Utility' must be selected as source!
|  | Voltage where AccuSine system is attached: |  |  |  | V |  |  |  |  | 'Generator' has been selected as the source. Entry of 'Generator' parameters is required!
[6 empty] | The PCC selected does not exist! Enter Electrical System Data for the selected PCC on the 'Electrical System 1-line' worksheet! |  |  |  |  | 'Generator' has been selected as the PCC. Entry of 'Generator' parameters is required! 'Generator' must be selected as source!
|  | Point of Common Coupling (PCC) |  | Utility | [6 empty] | 'Distribution Transformer - Secondary' has been chosen as the PCC below. Entry of transformer parameters is required on the 'Electrical System 1-line' worksheet!
|  | Harmonic Standard for current limits is |  |  |  | (optional) |  |  |  |  | 'MCC Transformer - Secondary' has been chosen as the PCC below. Entry of transformer parameters is required on the 'Electrical System 1-line' worksheet! | [12 empty] | 0
0
[11 empty] | 0 | 0 | 0 | 0 | [9 empty] | 0
| Applied operational mode(s): | [22 empty] | 0
| Harmonic Mitigation: |  |  | THDi Required: | [6 empty] | Selection of at least one operational mode is required! | [13 empty] | 0 |  |  |  |  | PWM VFD
| Power Factor Correction: |  |  | DPF (Cos φ) Required: | [6 empty] | Only 'Harmonic Mitigation' mode has been selected. No adjustment of 'Percent of AccuSine system assigned for Harmonic Mitigation' is required! | [12 empty] | 0 |  | 0 |  |  |  | VSI VFD
|  | Percent of AccuSine PCS system assigned for Harmonic Mitigation: | [22 empty] | 0 |  |  |  |  | AFE VFD
[11 empty] | 'Power Factor Correction' has been selected. An objective displacement PF (Cos phi) value must be entered. | [12 empty] | 0 | [5 empty] | DC drive
[24 empty] | 0 |  | 0 |  | 6 |  | DC power supply - Inductive
|  |  | Selection of at least one operational mode is required! | [7 empty] | The selected PCC does not exist! | [16 empty] | 12 |  | DC power supply - Resistive
[28 empty] | 18 |  | UPS w/Diode rectifier
Equipment list for NONLINEAR LOADS | [10 empty] | When Harmonic Mode is selected, either a 'Harmonic Standard' must be selected or 'TDD Required' value must be entered! TDD may be set as low as 3%. | [18 empty] | UPS w/SCR rectifier
Item | Quantity | Size | Unit of Measure | Type of Equipment |  | Rectifier pulses | Installed Impedance (%Z) | Maximum Capacity Utilized | Full Load Displacement PF | [20 empty] | UPS w/AFE rectifier
1 | [10 empty] | Adjustment of 'Percent Of AccuSine system assigned for Harmonic Mitigation' above may permit compliance with all objectives! | [18 empty] | UV power supply
2
3 | [10 empty] | When 'Load Balancing' is selected, an entry is required for "% mains current imbalance."
4
5 | [10 empty] | The 'Short Circuit Ratio (ShCR)' is very low. Be sure the loads do not exceed the electrical system capacity or the selected source has adequate short circuit capacity!
6
7
8
9
10 | [9 empty] | ShCA System | PCC SCA | [12 empty] | 0 | [13 empty] | Data Center /Cloud Farms Servers
[10 empty] | 0 | 0 |  | Connection Voltage = |  |  | 480 | [5 empty] | DPF indicator |  |  |  |  | Partial loading multiplier | [11 empty] | DPF (negative = leading PF) | [20 empty] | total same size
[10 empty] | ShCR1 | Unit ShCR | OPR KVA | I rms | TDD | %z | Ifund | Iharm | I reactive | Ireal |  |  |  | DPF | qty | size | 12-p | SCR RECT | [6 empty] | 12-p | 18-p |  | KW | KVA | [11 empty] | c37 | c38 | c39 | c40 | c41 | c42 | c43 | c44 | c45 | c46 |  | divisor
AC Motors Operating Direct-on-Line | [6 empty] | IEEE 519-2014 Table 2 |  |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 | [6 empty] | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Item | Quantity | Size | Unit of Measure | Rated Full Load PF (Nameplate) | Maximum Capacity Utilized |  | Isc/If FLA | % TDD |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 | 0 | 0 |  | Operating PF Table |  |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
11 | [6 empty] | <20 | 5% |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | % Max Ld | DPF |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
12 | [6 empty] | <50 | 8% |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 0 | 0.35 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
13 | [6 empty] | <100 | 12% |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 30 | 0.6 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
14 | [6 empty] | <1000 | 15% |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 40 | 0.74 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
15 | [6 empty] | >=1000 | 20% |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 50 | 0.84 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 75 | 0.97 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  |  |  | Equivalent installed impedance: |  | 0 | % |  |  | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 |  |  |  | 100 | 1 |  | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[10 empty] | 2501 | 2501 | 0 | 0 | 0% | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 |  | 1 | [6 empty] | 0 | 0 | [13 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Selection adjustment factor according to installed impedance: |  |  |  | 3 | [5 empty] | 0 | 0 |  |  | 0 | 0 | 0 | 0 | KVAfund | 0 |  | 0 | 0 |  | 0 | [7 empty] | 0 | 0
[20 empty] | Kw | 0 |  |  | 1.0309 |  | 0
|  |  | System Short Circuit Ratio (ShCR) @ selected PCC: |  |  | 2501 | :1 |  |  | Rated KVA | Rated KW | OPR kva | I fund | OPR KW | PF factor | Ifund |  | Ireactive | Ireal | [6 empty] | 0 | 0 | max % LD | Min % LD | Max DPF | Min DPF | Factor |  |  |  |  | Req'd | obj | A/S Adj Rating |  | Reset to 3% THDi |  |  |  | 3%
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | 0 | [15 empty] | TDD Req'd | 0% | 0 |  |  | 0 | 0% |  |  | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [16 empty] | Ih req'd | 0 |  | 0 |  | 0 | 0
[10 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [16 empty] | DPF req'd | 0 | 0 |  |  | G56 = | 3
|  |  | Uncorrected System | [6 empty] | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0 | [16 empty] | Ir req'd | 0 | 0%
|  |  | Type of RMS Current | Original System Current Amplitudes & Total Harmoic Current Distortion |  | Power |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0 |  | 0 | 0
|  |  | Total Irms | 0 | amps | 0 | KVA | [20 empty] | #REF! | #REF! | #REF! | #REF! | #REF! | Get from LB worksheet |  |  | Ilb req'd | 0 | 0% | [5 empty] | System Volts | 480
|  |  | Total Ifund | 0 | amps | 0 | KW |  |  | 0 |  | 0 | 0 |  | 0 | 0 |  | 0 | 0 | KVAfund | 0
|  |  | Total Ih | 0 | amps | 0 | Distortion PF |  |  | Total Currents - uncorrected |  |  | 0 |  | #DIV/0! | 0 | 0 | 0 | 0 | Tot KVA fund | 0 | [14 empty] | MIN Req'd AHF | 0 | @sys volt |  | Selected | 0 |  | 0
|  |  | Total Ireactive | 0 | amps | 0 | KVAR |  |  | total SCR | 0 |  |  |  |  | TDD orig | 0% | 0% | 0 | Original System PF | 0 | orig kW | [13 empty] | @base volts | 0 | [8 empty] | 0 | 0
|  |  | % THDi | 0% |  | 0 | Cos ɸ | (Displacement PF) | [7 empty] | Adj Harmonic current req'd | 0 | 0 | 0 | Objective PF | [8 empty] | 1 | [8 empty] | g30= | 0%
[6 empty] | 0 | Total PF |  |  |  | 0 | 20 |  |  |  | Reactive current correction req'd |  |  | 0 | Kvar req'd | 5% of NL loads | [14 empty] | According to Priority |  |  |  | 0 | 0
[36 empty] | Ih avail rating | 0 | harmonics |  | Attain Ih | 0 | TDD attain | 0%
|  |  | AccuSine+ rating required @ system bus voltage: |  |  | 0 | amps | [8 empty] | Load Balancing req'd |  |  | 0 | remaining | [15 empty] | available for Fund | 0 | fundamental | [9 empty] | 324.7765
[14 empty] | Req'd AccuSine | [21 empty] | If Req'd to meet obj | 0 | Ir avail | 0 |  | 0
|  |  | AccuSine+ rating required @ unit base voltage: |  |  | 0 | amps | [8 empty] | Req'd AccuSine at 480V |  | AccuSine voltage on sec xfo | 480 | [15 empty] | 0 | Ratio | 1
[16 empty] | Applied rating |  | @ voltage = | [18 empty] | 0
|  |  | User Selected AccuSine+ rating @ unit base voltage: |  |  |  | amps | [28 empty] | Adjusted Ir | 0 |  |  |  | orig TDD | 0% | Orig Ih | 0
[36 empty] | Adjusted PF | 0 |  |  |  | Adjusted TDD | #DIV/0!
|  |  | Corrected System | [35 empty] | Ikw | 0 | Orig If | 0 | Orig Irms | 0
|  |  | Type of RMS Current | Corrected Current Amplitudes & Total Harmoic Current Distortion |  | Corrected Power | [29 empty] | LB avail | 0 | [5 empty] | Orig Ir | 0
|  |  | Total Irms | 0 | amps | 0 | KVA | [28 empty] | LB Adj Amp | 0 | 0% |  |  | Adj If | 0 | Adj Irms | 0
|  |  | Total Ifund | 0 | amps | 0 | KW | [35 empty] | Adj Ir | 0
|  |  | Total Ih | 0 | amps | 0 | Distortion PF
|  |  | Total Ireactive | 0 | amps | 0 | KVAR
|  |  | % THDi (achieved) | 0% |  | 0 | Cos ɸ | (Displacement PF)
[6 empty] | 0 | Total PF
|  | Harmonic mitigation has not been selected. The harmonic distortion is |  |  |  |  | 0% | THDi
|  | This selection meets or exceeds the objective displacement PF [Cos ɸ] of | [5 empty] | DPF (Cos φ)
All results are estimates. Actual results may vary.
If there are any questions, please, consult your local Schneider Electric representative.
| AccuSine® is a registered trademark of Schneider Electric | [10 empty] | 0 | 0 |  | 0
This selection attains
This selection meets or exceeds the objective displacement PF [Cos ɸ] of
This selection fails to meet the objective displacement PF [Cos φ] of
unbalanced.
Based upon the data entered and the selection criteria chosen, no correction is required!
Note on E11: mpl649: Select the PCC that corresponds to one of the levels defined on 'Electrical System 1-line' worksheet.
Note on F13: mpl649: Select one if compliance to a standard is required. If none apply, select 'Harmonic Mitigation' mode and enter a value for 'TDD Required' below.
Note on E25: mpl649: Select the nonlinear load type from the drop down menu.
Note on G25: mpl649: Select the number of pulses for each load from the drop down menu.
Note on H25: mpl649: For PWM VFD enter known impedance of DC Bus Choke or Input Line Reactor or sum of both if present. PWM VFD 'Default' is the standard SE ATV 61/71 unit impedance according to size entered. Make no entry when 12-p or 18-p is selected. For all other types of loads, enter the impedance of input line reactors, if present.
Note on I25: mpl649: Enter the maximum level of capacity utilized for the application. For PWM VFD LOADS: 1. For centrifugal pumps and fans, a conservative value is 80%. 2. For constant torque loads, 100% is most likely. Default is 100%.
Note on J25: mpl649: Default DPF for diode reactifiers is 0.95 and for AFE rectifers is 0.99. For Thyristor rectifiers enter design DPF at full load. If in doubt leave it blank - default is 0.95.
Note on E39: mpl649: Enter power factor as 0.xx. Entry cannot be greater than 1.
Note on F39: mpl649: Enter the maximum level of capacity utilized for each application.
Note on G65: mpl649: When a transformer is used to affix AccuSine to a voltage higher than 690 VAC design, the required AccuSine system rating is increased by the transformer voltage ratio.
Note on G67: mpl649: Enter the next higher integer greater than the calculated value shown above in "AccuSine rating required @ unit base voltage" (blue cell directly above) to obtain optimized results. Any value can be entered if so desired.

## Server
Selection of AccuSine+® Rating for Server Applications
Customer Name: | [7 empty] | Date: | 0
Project Name: | [5 empty] | Project ID:
Complete 'Electrical System 1-line' worksheet to set VAC.
| Servers for Data Centers and Cloud Farms | [5 empty] | AC Voltage = |  | 0 | VAC |  |  | Server Calculations |  |  | 0 |  | THDi = | 0.05
| Item | Qty | KW rating | Design DPF @ Full Load (leading) | Part Load Expectation | Required PF for site (leading) | [6 empty] | design kw | OPR KW | kva at design | kvar at Design | oper PF | kvar at operating level | KVAR site req'd | KVAR Correction | Amps at Req'd corrected
| 1 | [10 empty] | 1 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 2 | [10 empty] | 2 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 3 | [10 empty] | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| 4 | [10 empty] | 4 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
| Note: All displacement PF values are leading. They must be entered as negative values above. | [10 empty] | totals | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | #DIV/0!
[12 empty] | current | #DIV/0! | #DIV/0! | #DIV/0! | #DIV/0! |  | #DIV/0! | #DIV/0! | #DIV/0!
[16 empty] | DF | 0.99875
|  |  | Uncorrected System | [12 empty] | TPF | 0 |  |  | Ir result | #DIV/0!
|  |  | Type of RMS Current | Original System Current Amplitudes & Total Harmoic Current Distortion |  | Power | [6 empty] | Uncorrected |  |  |  | Corrected
|  |  | Total Irms | #DIV/0! | amps | #DIV/0! | KVA | [5 empty] | total KVA | #DIV/0! | Irms | #DIV/0! | Irms | #DIV/0! | total KVA | #DIV/0!
|  |  | Total Ifund | #DIV/0! | amps | #DIV/0! | KW | [5 empty] | KVA | #DIV/0! | Ifund | #DIV/0! | Ifund | #DIV/0! | KVA | #DIV/0! | req'd AccuISne Ir
|  |  | Total Ih | #DIV/0! | amps | #DIV/0! | Distortion PF | [5 empty] | KVAR | 0 | Ireactive | #DIV/0! | Ireactive | #DIV/0! | KVAR | #DIV/0! | #DIV/0! |  | #DIV/0!
|  |  | Total Ireactive | #DIV/0! | amps | #DIV/0! | KVAR | [5 empty] | Kh | #DIV/0! | Iharm | #DIV/0! | Iharm | #DIV/0! |  | #DIV/0!
|  |  | % THDi | #DIV/0! |  | #DIV/0! | Cos ɸ | (Displacement PF) |  |  | #DIV/0! | [10 empty] | Applied | 0
[6 empty] | #DIV/0! | Total PF | [5 empty] | KW | #DIV/0! | Ikw | #DIV/0! | Ikw | #DIV/0! | KW | #DIV/0!
[17 empty] | %THDI | #DIV/0! |  |  |  | Adj Ir result | #DIV/0! | KVAR | #DIV/0!
|  |  | AccuSine rating required @ system bus voltage: |  |  | #DIV/0! | amps |  |  |  | #DIV/0! | [10 empty] | Adj Ifund | #DIV/0! | KVA | #DIV/0!
[22 empty] | Adj Total Irms | #DIV/0! | total KVA | #DIV/0!
|  |  | AccuSine rating required @ unit base voltage: |  |  | #DIV/0! | amps
[22 empty] | Cos φ = | #DIV/0!
|  |  | User Selected AccuSine rating @ unit base voltage: |  |  |  | amps
Corrected System
|  |  | Type of RMS Current | Corrected Current Amplitudes & Total Harmoic Current Distortion |  | Corrected Power
|  |  | Total Irms | #DIV/0! | amps | #DIV/0! | KVA
|  |  | Total Ifund | #DIV/0! | amps | #DIV/0! | KW
|  |  | Total Ih | #DIV/0! | amps | #DIV/0! | Distortion PF
|  |  | Total Ireactive | #DIV/0! | amps | #DIV/0! | KVAR
|  |  | % THDi (achieved) | #DIV/0! |  | #DIV/0! | Cos ɸ | (Displacement PF)
[6 empty] | #DIV/0! | Total PF
#DIV/0!
Note on G28: mpl649: When a transformer is used to affix AccuSine to a voltage higher than 690 VAC design, the required AccuSine system rating is increased by the transformer voltage ratio.
Note on G30: mpl649: Enter the next higher integer greater than the calculated value shown above in "AccuSine rating required @ unit base voltage" (blue cell directly above) to obtain optimized results. Any value can be entered if so desired.

## Model Selector
AccuSine+® Unit BOM
Customer Name: | [5 empty] | Date:
AccuSine system voltage: |  | 480 | VAC
[6 empty] | Modes Selected | [5 empty] | yes | x
User selection @ unit base voltage |  | 0 | [9 empty] | no
Is your selction for Server loads? |  | no
Altitude (adjust when altitude exceeds 1000 meters): |  | 1000 | Meters (Cannot exceed 4800m.) Derate at 1% per 100m over 1000m.
Ambient temperature adjustment for AccuSine PCS+ and AccuSine PFV+: |  | 40 | °C | AccuSine PCS+/PFV+ IP00 and IP20 models rated 60A, 120A, & 200A are 100% continuous duty to 45°C; All other ratings and enclosures are 100% continuous duty to 40°C. Maximum ambient is 50°C for all models. Absolute shut down occurs at 51°C inlet air temperature.
Enclosure type required: (select using an 'x') SELECT ONLY ONE! |  |  | IP00 (chassis)
|  |  | IP20 (Wall mount UL Type 1) |  | An enclosure type must be selected!
IP31
IP54
UL Type 2 (Drip proof)
UL Type 12
AccuSine+ Model Selection
| Model Selection is based upon user selected rating, ambient temperature, altitude, and enclosure type. | [6 empty] | Select | Model 1 | Model 2 | QTY 1 | QTY 2
| Item | Quantity | Model Number | Description |  |  | 0 | A | 0 | 0 | 0 | 0
[7 empty] | 0 | B | 0 | 0 | 0 | 0
[7 empty] | 0 | C | 0 | 0 | 0 | 0
[7 empty] | 0 | D | 0 | 0 | 0 | 0
[7 empty] | 0 | E | 0 | 0 | 0 | 0 |  | #N/A
[7 empty] | 0 | F | 0 | 0 | 0 | 0
[7 empty] | 0 | G | 0 | 0 | 0 | 0
If there are any questions, please, consult your local Schneider Electric representative.
Note on D12: mpl649: Enter altitude if 1000 meters is exceeded.
Note on D13: mpl649: Enter temperature if 40 degrees C is exceeded. 50 degrees C is maximum possible ambient temperature.

## Mod Sel Calcs (hidden)
[20 empty] | Model # | Description
[6 empty] | Voltage adjustment |  |  | 240 | AccuSine PCS | IP00 | IP31 | IP54 | UL Type 2 | UL Type 12 |  |  |  |  | EVCP040D7IP31 | AccuSine PFV+ 40A, 600-690 VAC IP31
|  |  | AMPS Selected @ voltage |  | 0 |  |  |  | 60 | 60 | PCSP060D2IP00 | PCSP060D2IP31 | PCSP060D2IP54 | PCSP060D2N2 | PCSP060D2N12 |  |  |  |  | EVCP040D7IP54 | AccuSine PFV+ 40A, 600-690 VAC IP54
|  |  | 60/120/200 IP00 | 300A | all enclosures | 1 | PFV |  | 120 | 120 | PCSP120D2IP00 | PCSP120D2IP31 | PCSP120D2IP54 | PCSP120D2N2 | PCSP120D2N12 |  |  |  |  | EVCP040D7N12 | AccuSine PFV+ 40A, 600-690 VAC N12
alt | derate |  | 1 | [5 empty] | 200 | 200 | PCSP200D2IP00 | PCSP200D2IP31 | PCSP200D2IP54 | PCSP200D2N2 | PCSP200D2N12 |  |  |  |  | EVCP040D7N2 | AccuSine PFV+ 40A, 600-690 VAC N2
temp | derate |  | 1 | 1 | 1 |  |  |  | 300 | 300 | PCSP300D2IP00 | PCSP300D2IP31 | PCSP300D2IP54 | PCSP300D2N2 | PCSP300D2N12 |  |  |  |  | EVCP047D6IP31 | AccuSine PFV+ 47A, 480-600 VAC IP31
|  |  | 45C | 40C | 40C | [14 empty] | EVCP047D6IP54 | AccuSine PFV+ 47A, 480-600 VAC IP54
|  |  |  | yes |  |  |  |  | 480 | AccuSine PCS | IP00 | IP31 | IP54 | UL Type 2 | UL Type 12 |  |  |  |  | EVCP047D6N12 | AccuSine PFV+ 47A, 480-600 VAC N12
|  |  |  | no | 0 |  |  |  | 60 | 60 | PCSP060D5IP00 | PCSP060D5IP31 | PCSP060D5IP54 | PCSP060D5N2 | PCSP060D5N12 |  |  |  |  | EVCP047D6N2 | AccuSine PFV+ 47A, 480-600 VAC N2
[5 empty] | 0 |  |  |  | 120 | 120 | PCSP120D5IP00 | PCSP120D5IP31 | PCSP120D5IP54 | PCSP120D5N2 | PCSP120D5N12 |  |  |  |  | EVCP060D2IP00 | AccuSine PFV+ 60A 208-240V IP00
|  | 240V Selection |  | 0 | 0 |  |  |  | 200 | 200 | PCSP200D5IP00 | PCSP200D5IP31 | PCSP200D5IP54 | PCSP200D5N2 | PCSP200D5N12 |  |  |  |  | EVCP060D2IP00 | AccuSine PFV+ 60A 208-240V IP00
|  |  | 480VAC selection | 0 | 0 |  |  |  | 300 | 300 | PCSP300D5IP00 | PCSP300D5IP31 | PCSP300D5IP54 | PCSP300D5N2 | PCSP300D5N12 |  |  |  |  | EVCP060D2IP31 | AccuSine PFV+ 60A 208-240V IP31
|  |  | 600 VAC | 0 | 0 | [14 empty] | EVCP060D2IP31 | AccuSine PFV+ 60A 208-240V IP31
|  |  | 690 VAC | 0 | 0 |  |  |  | 600 | AccuSine PCS | IP31 | IP54 | UL Type 2 | UL Type 12 | [5 empty] | EVCP060D2IP54 | AccuSine PFV+ 60A 208-240V IP54
[5 empty] | 0 |  |  |  | 47 | 47 | PCSP047D6IP31 | PCSP047D6IP54 | PCSP047D6N2 | PCSP047D6N12 | [5 empty] | EVCP060D2IP54 | AccuSine PFV+ 60A 208-240V IP54
[5 empty] | 0 |  |  |  | 94 | 94 | PCSP094D6IP31 | PCSP094D6IP54 | PCSP094D6N2 | PCSP094D6N12 | [5 empty] | EVCP060D2N12 | AccuSine PFV+ 60A 208-240V N12
[5 empty] | 0 |  |  |  | 157 | 157 | PCSP157D6IP31 | PCSP157D6IP54 | PCSP157D6N2 | PCSP157D6N12 | [5 empty] | EVCP060D2N12 | AccuSine PFV+ 60A 208-240V N12
yes | [8 empty] | 235 | 235 | PCSP235D6IP31 | PCSP235D6IP54 | PCSP235D6N2 | PCSP235D6N12 | [5 empty] | EVCP060D2N2 | AccuSine PFV+ 60A 208-240V N2
no | [8 empty] | 690 | AccuSine PCS | IP31 | IP54 | UL Type 2 | UL Type 12 | [5 empty] | EVCP060D2N2 | AccuSine PFV+ 60A 208-240V N2
[9 empty] | 40 | 40 | PCSP040D7IP31 | PCSP040D7IP54 | PCSP040D7N2 | PCSP040D7N12 | [5 empty] | EVCP060D5IP00 | AccuSine PFV+ 60A, 380-480 VAC IP00
[9 empty] | 80 | 80 | PCSP080D7IP31 | PCSP080D7IP54 | PCSP080D7N2 | PCSP080D7N12 | [5 empty] | EVCP060D5IP31 | AccuSine PFV+ 60A, 380-480 VAC IP31
[9 empty] | 133 | 133 | PCSP133D7IP31 | PCSP133D7IP54 | PCSP133D7N2 | PCSP133D7N12 | [5 empty] | EVCP060D5IP54 | AccuSine PFV+ 60A, 380-480 VAC IP54
[9 empty] | 200 | 200 | PCSP200D7IP31 | PCSP200D7IP54 | PCSP200D7N2 | PCSP200D7N12 | [5 empty] | EVCP060D5N12 | AccuSine PFV+ 60A, 380-480 VAC N12
[20 empty] | EVCP060D5N2 | AccuSine PFV+ 60A, 380-480 VAC N2
[9 empty] | 240 | AccuSine PFV | IP00 | IP31 | IP54 | UL Type 2 | UL Type 12 |  |  |  |  | EVCP080D7IP31 | AccuSine PFV+ 80A, 600-690 VAC IP31
[9 empty] | 60 | 60 | EVCP060D2IP00 | EVCP060D2IP31 | EVCP060D2IP54 | EVCP060D2N2 | EVCP060D2N12 |  |  |  |  | EVCP080D7IP54 | AccuSine PFV+ 80A, 600-690 VAC IP54
[9 empty] | 120 | 120 | EVCP120D2IP00 | EVCP120D2IP31 | EVCP120D2IP54 | EVCP120D2N2 | EVCP120D2N12 |  |  |  |  | EVCP080D7N12 | AccuSine PFV+ 80A, 600-690 VAC N12
[9 empty] | 200 | 200 | EVCP200D2IP00 | EVCP200D2IP31 | EVCP200D2IP54 | EVCP200D2N2 | EVCP200D2N12 |  |  |  |  | EVCP080D7N2 | AccuSine PFV+ 80A, 600-690 VAC N2
[9 empty] | 300 | 300 | EVCP300D2IP00 | EVCP300D2IP31 | EVCP300D2IP54 | EVCP300D2N2 | EVCP300D2N12 |  |  |  |  | EVCP094D6IP31 | AccuSine PFV+ 94A, 480-600 VAC IP31
[9 empty] | 480 | AccuSine PFV | IP00 | IP31 | IP54 | UL Type 2 | UL Type 12 |  |  |  |  | EVCP094D6IP54 | AccuSine PFV+ 94A, 480-600 VAC IP54
[9 empty] | 60 | 60 | EVCP060D5IP00 | EVCP060D5IP31 | EVCP060D5IP54 | EVCP060D5N2 | EVCP060D5N12 |  |  |  |  | EVCP094D6N12 | AccuSine PFV+ 94A, 480-600 VAC N12
[9 empty] | 120 | 120 | EVCP120D5IP00 | EVCP120D5IP31 | EVCP120D5IP54 | EVCP120D5N2 | EVCP120D5N12 |  |  |  |  | EVCP094D6N2 | AccuSine PFV+ 94A, 480-600 VAC N2
[9 empty] | 200 | 200 | EVCP200D5IP00 | EVCP200D5IP31 | EVCP200D5IP54 | EVCP200D5N2 | EVCP200D5N12 |  |  |  |  | EVCP120D2IP00 | AccuSine PFV+ 120A 208-240V IP00
[9 empty] | 300 | 300 | EVCP300D5IP00 | EVCP300D5IP31 | EVCP300D5IP54 | EVCP300D5N2 | EVCP300D5N12 |  |  |  |  | EVCP120D2IP00 | AccuSine PFV+ 120A 208-240V IP00
[20 empty] | EVCP120D2IP31 | AccuSine PFV+ 120A 208-240V IP31
[20 empty] | EVCP120D2IP31 | AccuSine PFV+ 120A 208-240V IP31
[9 empty] | 600 | AccuSine PFV | IP31 | IP54 | UL Type 2 | UL Type 12 | [5 empty] | EVCP120D2IP54 | AccuSine PFV+ 120A 208-240V IP54
[9 empty] | 47 | 47 | EVCP047D6IP31 | EVCP047D6IP54 | EVCP047D6N2 | EVCP047D6N12 | [5 empty] | EVCP120D2IP54 | AccuSine PFV+ 120A 208-240V IP54
[9 empty] | 94 | 94 | EVCP094D6IP31 | EVCP094D6IP54 | EVCP094D6N2 | EVCP094D6N12 | [5 empty] | EVCP120D2N12 | AccuSine PFV+ 120A 208-240V N12
[9 empty] | 157 | 157 | EVCP157D6IP31 | EVCP157D6IP54 | EVCP157D6N2 | EVCP157D6N12 | [5 empty] | EVCP120D2N12 | AccuSine PFV+ 120A 208-240V N12
[9 empty] | 235 | 235 | EVCP235D6IP31 | EVCP235D6IP54 | EVCP235D6N2 | EVCP235D6N12 | [5 empty] | EVCP120D2N2 | AccuSine PFV+ 120A 208-240V N2
|  | voltage selection | [17 empty] | EVCP120D2N2 | AccuSine PFV+ 120A 208-240V N2
| PCS/PFV | 480 | [6 empty] | 690 | AccuSine PFV | IP31 | IP54 | UL Type 2 | UL Type 12 | [5 empty] | EVCP120D5IP00 | AccuSine PFV+ 120A, 380-480 VAC IP00
[9 empty] | 40 | 40 | EVCP040D7IP31 | EVCP040D7IP54 | EVCP040D7N2 | EVCP040D7N12 | [5 empty] | EVCP120D5IP31 | AccuSine PFV+ 120A, 380-480 VAC IP31
[9 empty] | 80 | 80 | EVCP080D7IP31 | EVCP080D7IP54 | EVCP080D7N2 | EVCP080D7N12 | [5 empty] | EVCP120D5IP54 | AccuSine PFV+ 120A, 380-480 VAC IP54
[9 empty] | 133 | 133 | EVCP133D7IP31 | EVCP133D7IP54 | EVCP133D7N2 | EVCP133D7N12 | [5 empty] | EVCP120D5N12 | AccuSine PFV+ 120A, 380-480 VAC N12
[9 empty] | 200 | 200 | EVCP200D7IP31 | EVCP200D7IP54 | EVCP200D7N2 | EVCP200D7N12 | [5 empty] | EVCP120D5N2 | AccuSine PFV+ 120A, 380-480 VAC N2
[20 empty] | EVCP133D7IP31 | AccuSine PFV+ 133A, 600-690 VAC IP31
|  |  |  | Model Selection | d8 Revised | V | Encl |  | Criteria for PCS or PFV | 1 |  |  |  | qty 1 | qty 2 |  |  |  |  | EVCP133D7IP54 | AccuSine PFV+ 133A, 600-690 VAC IP54
[10 empty] | model 1 | model 2 | 301 |  | 2 |  |  |  | Enclosure selection |  | EVCP133D7N12 | AccuSine PFV+ 133A, 600-690 VAC N12
|  |  |  | 0 | 0 | 480 |  | AccuSine PCS 240V |  | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP133D7N2 | AccuSine PFV+ 133A, 600-690 VAC N2
[16 empty] | Rdup | rddn |  | if IP20 | EVCP157D6IP31 | AccuSine PFV+ 157A, 480-600 VAC IP31
|  |  |  | 0 | 0 | 480 |  | AccuSine PCS 480V |  | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP157D6IP54 | AccuSine PFV+ 157A, 480-600 VAC IP54
[20 empty] | EVCP157D6N12 | AccuSine PFV+ 157A, 480-600 VAC N12
|  |  |  | 0 | 0 | 480 |  | AccuSine PCS 600V |  | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP157D6N2 | AccuSine PFV+ 157A, 480-600 VAC N2
[20 empty] | EVCP200D2IP00 | AccuSine PFV+ 200A 208-240V IP00
|  |  |  | 0 | 0 | 480 |  | AccuSine PCS 690V |  | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP200D2IP00 | AccuSine PFV+ 200A 208-240V IP00
[20 empty] | EVCP200D2IP31 | AccuSine PFV+ 200A 208-240V IP31
|  |  |  | 0 | 0 | 480 |  | AccuSine PFV 240V |  | 0 | 0 | #VALUE! | #VALUE! | 0 | 0 | 0 | 0 |  |  | EVCP200D2IP31 | AccuSine PFV+ 200A 208-240V IP31
[20 empty] | EVCP200D2IP54 | AccuSine PFV+ 200A 208-240V IP54
|  |  |  | 0 | 0 | 480 |  | AccuSine PFV 480V |  | 0 | 0 | 61 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP200D2IP54 | AccuSine PFV+ 200A 208-240V IP54
[20 empty] | EVCP200D2N12 | AccuSine PFV+ 200A 208-240V N12
|  |  |  | 0 | 0 | 480 |  | AccuSine PFV 600V |  | 0 | 0 | 48 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP200D2N12 | AccuSine PFV+ 200A 208-240V N12
[20 empty] | EVCP200D2N2 | AccuSine PFV+ 200A 208-240V N2
|  |  |  | 0 | 0 | 480 |  | AccuSine PFV 690 |  | 0 | 0 | 41 | 0 | 0 | 0 | 0 | 0 |  |  | EVCP200D2N2 | AccuSine PFV+ 200A 208-240V N2
[20 empty] | EVCP200D5IP00 | AccuSine PFV+ 200A, 380-480 VAC IP00
[20 empty] | EVCP200D5IP31 | AccuSine PFV+ 200A, 380-480 VAC IP31
[20 empty] | EVCP200D5IP54 | AccuSine PFV+ 200A, 380-480 VAC IP54
[20 empty] | EVCP200D5N12 | AccuSine PFV+ 200A, 380-480 VAC N12
[20 empty] | EVCP200D5N2 | AccuSine PFV+ 200A, 380-480 VAC N2
[20 empty] | EVCP200D7IP31 | AccuSine PFV+ 200A, 600-690 VAC IP31
[20 empty] | EVCP200D7IP54 | AccuSine PFV+ 200A, 600-690 VAC IP54
[20 empty] | EVCP200D7N12 | AccuSine PFV+ 200A, 600-690 VAC N12
[20 empty] | EVCP200D7N2 | AccuSine PFV+ 200A, 600-690 VAC N2
[20 empty] | EVCP235D6IP31 | AccuSine PFV+ 235A, 480-600 VAC IP31
[20 empty] | EVCP235D6IP54 | AccuSine PFV+ 235A, 480-600 VAC IP54
[20 empty] | EVCP235D6N12 | AccuSine PFV+ 235A, 480-600 VAC N12
[20 empty] | EVCP235D6N2 | AccuSine PFV+ 235A, 480-600 VAC N2
[20 empty] | EVCP300D2IP00 | AccuSine PFV+ 300A 208-240V IP00
[20 empty] | EVCP300D2IP00 | AccuSine PFV+ 300A 208-240V IP00
[20 empty] | EVCP300D2IP31 | AccuSine PFV+ 300A 208-240V IP31
[20 empty] | EVCP300D2IP31 | AccuSine PFV+ 300A 208-240V IP31
|  |  |  | PCSPWMKIT60A | AccuSine+ Wall Mount Conversion Kit 60A | [14 empty] | EVCP300D2IP54 | AccuSine PFV+ 300A 208-240V IP54
|  |  |  | PCSPWMKIT120A | AccuSine+ Wall Mount Conversion Kit 120A | [14 empty] | EVCP300D2IP54 | AccuSine PFV+ 300A 208-240V IP54
|  |  |  | PCSPWMKIT300A | AccuSine+ Wall Mount Conversion Kit 200-300A | [14 empty] | EVCP300D2N12 | AccuSine PFV+ 300A 208-240V N12
[20 empty] | EVCP300D2N12 | AccuSine PFV+ 300A 208-240V N12
[20 empty] | EVCP300D2N2 | AccuSine PFV+ 300A 208-240V N2
[20 empty] | EVCP300D2N2 | AccuSine PFV+ 300A 208-240V N2
|  |  | Item 1 | FALSE | [15 empty] | EVCP300D5IP00 | AccuSine PFV+ 300A, 380-480 VAC IP00
|  |  |  | FALSE | [15 empty] | EVCP300D5IP31 | AccuSine PFV+ 300A, 380-480 VAC IP31
[20 empty] | EVCP300D5IP54 | AccuSine PFV+ 300A, 380-480 VAC IP54
|  |  | Item 2 | FALSE | [15 empty] | EVCP300D5N12 | AccuSine PFV+ 300A, 380-480 VAC N12
|  |  |  | FALSE | [15 empty] | EVCP300D5N2 | AccuSine PFV+ 300A, 380-480 VAC N2
[20 empty] | PCSP040D7IP31 | AccuSine PCS+ 40A, 600-690 VAC IP31
[20 empty] | PCSP040D7IP54 | AccuSine PCS+ 40A, 600-690 VAC IP54
[20 empty] | PCSP040D7N12 | AccuSine PCS+ 40A, 600-690 VAC N12
[20 empty] | PCSP040D7N2 | AccuSine PCS+ 40A, 600-690 VAC N2
[20 empty] | PCSP047D6IP31 | AccuSine PCS+ 47A, 480-600 VAC IP31
[20 empty] | PCSP047D6IP54 | AccuSine PCS+ 47A, 480-600 VAC IP54
[20 empty] | PCSP047D6N12 | AccuSine PCS+ 47A, 480-600 VAC N12
[20 empty] | PCSP047D6N2 | AccuSine PCS+ 47A, 480-600 VAC N2
[20 empty] | PCSP060D2IP00 | AccuSine PCS+ 60A 208-240V IP00
[20 empty] | PCSP060D2IP00 | AccuSine PCS+ 60A 208-240V IP00
[20 empty] | PCSP060D2IP31 | AccuSine PCS+ 60A 208-240V IP31
[20 empty] | PCSP060D2IP31 | AccuSine PCS+ 60A 208-240V IP31
[20 empty] | PCSP060D2IP54 | AccuSine PCS+ 60A 208-240V IP54
[20 empty] | PCSP060D2IP54 | AccuSine PCS+ 60A 208-240V IP54
[20 empty] | PCSP060D2N12 | AccuSine PCS+ 60A 208-240V N12
[20 empty] | PCSP060D2N12 | AccuSine PCS+ 60A 208-240V N12
[20 empty] | PCSP060D2N2 | AccuSine PCS+ 60A 208-240V N2
[20 empty] | PCSP060D2N2 | AccuSine PCS+ 60A 208-240V N2
[20 empty] | PCSP060D5IP00 | AccuSine PCS+ 60A, 380-480 VAC IP00
[20 empty] | PCSP060D5IP31 | AccuSine PCS+ 60A, 380-480 VAC IP31
[20 empty] | PCSP060D5IP54 | AccuSine PCS+ 60A, 380-480 VAC IP54
[20 empty] | PCSP060D5N12 | AccuSine PCS+ 60A, 380-480 VAC N12
[20 empty] | PCSP060D5N2 | AccuSine PCS+ 60A, 380-480 VAC N2
[20 empty] | PCSP080D7IP31 | AccuSine PCS+ 80A, 600-690 VAC IP31
[20 empty] | PCSP080D7IP54 | AccuSine PCS+ 80A, 600-690 VAC IP54
[20 empty] | PCSP080D7N12 | AccuSine PCS+ 80A, 600-690 VAC N12
[20 empty] | PCSP080D7N2 | AccuSine PCS+ 80A, 600-690 VAC N2
[20 empty] | PCSP094D6IP31 | AccuSine PCS+ 94A, 480-600 VAC IP31
[20 empty] | PCSP094D6IP54 | AccuSine PCS+ 94A, 480-600 VAC IP54
[20 empty] | PCSP094D6N12 | AccuSine PCS+ 94A, 480-600 VAC N12
[20 empty] | PCSP094D6N2 | AccuSine PCS+ 94A, 480-600 VAC N2
[20 empty] | PCSP120D2IP00 | AccuSine PCS+ 120A 208-240V IP00
[20 empty] | PCSP120D2IP00 | AccuSine PCS+ 120A 208-240V IP00
[20 empty] | PCSP120D2IP31 | AccuSine PCS+ 120A 208-240V IP31
[20 empty] | PCSP120D2IP31 | AccuSine PCS+ 120A 208-240V IP31
[20 empty] | PCSP120D2IP54 | AccuSine PCS+ 120A 208-240V IP54
[20 empty] | PCSP120D2IP54 | AccuSine PCS+ 120A 208-240V IP54
[20 empty] | PCSP120D2N12 | AccuSine PCS+ 120A 208-240V N12
[20 empty] | PCSP120D2N12 | AccuSine PCS+ 120A 208-240V N12
[20 empty] | PCSP120D2N2 | AccuSine PCS+ 120A 208-240V N2
[20 empty] | PCSP120D2N2 | AccuSine PCS+ 120A 208-240V N2
[20 empty] | PCSP120D5IP00 | AccuSine PCS+ 120A, 380-480 VAC IP00
[20 empty] | PCSP120D5IP31 | AccuSine PCS+ 120A, 380-480 VAC IP31
[20 empty] | PCSP120D5IP54 | AccuSine PCS+ 120A, 380-480 VAC IP54
[20 empty] | PCSP120D5N12 | AccuSine PCS+ 120A, 380-480 VAC N12
[20 empty] | PCSP120D5N2 | AccuSine PCS+ 120A, 380-480 VAC N2
[20 empty] | PCSP133D7IP31 | AccuSine PCS+ 133A, 600-690 VAC IP31
[20 empty] | PCSP133D7IP54 | AccuSine PCS+ 133A, 600-690 VAC IP54
[20 empty] | PCSP133D7N12 | AccuSine PCS+ 133A, 600-690 VAC N12
[20 empty] | PCSP133D7N2 | AccuSine PCS+ 133A, 600-690 VAC N2
[20 empty] | PCSP157D6IP31 | AccuSine PCS+ 157A, 480-600 VAC IP31
[20 empty] | PCSP157D6IP54 | AccuSine PCS+ 157A, 480-600 VAC IP54
[20 empty] | PCSP157D6N12 | AccuSine PCS+ 157A, 480-600 VAC N12
[20 empty] | PCSP157D6N2 | AccuSine PCS+ 157A, 480-600 VAC N2
[20 empty] | PCSP200D2IP00 | AccuSine PCS+ 200A 208-240V IP00
[20 empty] | PCSP200D2IP00 | AccuSine PCS+ 200A 208-240V IP00
[20 empty] | PCSP200D2IP31 | AccuSine PCS+ 200A 208-240V IP31
[20 empty] | PCSP200D2IP31 | AccuSine PCS+ 200A 208-240V IP31
[20 empty] | PCSP200D2IP54 | AccuSine PCS+ 200A 208-240V IP54
[20 empty] | PCSP200D2IP54 | AccuSine PCS+ 200A 208-240V IP54
[20 empty] | PCSP200D2N12 | AccuSine PCS+ 200A 208-240V N12
[20 empty] | PCSP200D2N12 | AccuSine PCS+ 200A 208-240V N12
[20 empty] | PCSP200D2N2 | AccuSine PCS+ 200A 208-240V N2
[20 empty] | PCSP200D2N2 | AccuSine PCS+ 200A 208-240V N2
[20 empty] | PCSP200D5IP00 | AccuSine PCS+ 200A, 380-480 VAC IP00
[20 empty] | PCSP200D5IP31 | AccuSine PCS+ 200A, 380-480 VAC IP31
[20 empty] | PCSP200D5IP54 | AccuSine PCS+ 200A, 380-480 VAC IP54
[20 empty] | PCSP200D5N12 | AccuSine PCS+ 200A, 380-480 VAC N12
[20 empty] | PCSP200D5N2 | AccuSine PCS+ 200A, 380-480 VAC N2
[20 empty] | PCSP200D7IP31 | AccuSine PCS+ 200A, 600-690 VAC IP31
[20 empty] | PCSP200D7IP54 | AccuSine PCS+ 200A, 600-690 VAC IP54
[20 empty] | PCSP200D7N12 | AccuSine PCS+ 200A, 600-690 VAC N12
[20 empty] | PCSP200D7N2 | AccuSine PCS+ 200A, 600-690 VAC N2
[20 empty] | PCSP235D6IP31 | AccuSine PCS+ 235A, 480-600 VAC IP31
[20 empty] | PCSP235D6IP54 | AccuSine PCS+ 235A, 480-600 VAC IP54
[20 empty] | PCSP235D6N12 | AccuSine PCS+ 235A, 480-600 VAC N12
[20 empty] | PCSP235D6N2 | AccuSine PCS+ 235A, 480-600 VAC N2
[20 empty] | PCSP300D2IP00 | AccuSine PCS+ 300A 208-240V IP00
[20 empty] | PCSP300D2IP00 | AccuSine PCS+ 300A 208-240V IP00
[20 empty] | PCSP300D2IP31 | AccuSine PCS+ 300A 208-240V IP31
[20 empty] | PCSP300D2IP31 | AccuSine PCS+ 300A 208-240V IP31
[20 empty] | PCSP300D2IP54 | AccuSine PCS+ 300A 208-240V IP54
[20 empty] | PCSP300D2IP54 | AccuSine PCS+ 300A 208-240V IP54
[20 empty] | PCSP300D2N12 | AccuSine PCS+ 300A 208-240V N12
[20 empty] | PCSP300D2N12 | AccuSine PCS+ 300A 208-240V N12
[20 empty] | PCSP300D2N2 | AccuSine PCS+ 300A 208-240V N2
[20 empty] | PCSP300D2N2 | AccuSine PCS+ 300A 208-240V N2
[20 empty] | PCSP300D5IP00 | AccuSine PCS+ 300A, 380-480 VAC IP00
[20 empty] | PCSP300D5IP31 | AccuSine PCS+ 300A, 380-480 VAC IP31
[20 empty] | PCSP300D5IP54 | AccuSine PCS+ 300A, 380-480 VAC IP54
[20 empty] | PCSP300D5N12 | AccuSine PCS+ 300A, 380-480 VAC N12
[20 empty] | PCSP300D5N2 | AccuSine PCS+ 300A, 380-480 VAC N2
[20 empty] | PCSPWMKIT120A | AccuSine+ Wall Mount Conversion Kit 120A
[20 empty] | PCSPWMKIT300A | AccuSine+ Wall Mount Conversion Kit 200-300A
[20 empty] | PCSPWMKIT60A | AccuSine+ Wall Mount Conversion Kit 60A

## CT Selector
AccuSine+® Current Transformer (CT) Selection | [6 empty] | Reference Number | Description |  |  |  | Round |  | Reference Number | Description |  |  |  |  | Rectangular
[6 empty] | Primary Rating |  |  | Core Type | Mounting | Secondary Rating | Diameter (mm) | Primary Rating |  |  | Core Type | Mounting |  | Secondary Rating | Width (mm) | Height (mm) | PCSPCT7RL1021 | CURRENT TRANSFORMER 1000 1 SOLID RD 2.5ID
Project Name: |  |  |  |  | Date: | 200 | PCSPCT7RL2011 | CURRENT TRANSFORMER 200 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL1025 | CURRENT TRANSFORMER 1000 5 SOLID RD 2.5ID
[6 empty] | 300 | PCSPCT7RL3011 | CURRENT TRANSFORMER 300 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL1221 | CURRENT TRANSFORMER 1200 1 SOLID RD 2.5ID
There are many ratings and styles of CT available. This selector is based upon standard designs offered by Schneider Electric. Additional sizes and styles are available but not included in this selector. AccuSine PSC+ and AccuSine PFV+ can operate with 2 CT. If single phase loads are present, 3 CT are required. | [5 empty] | 400 | PCSPCT7RL4011 | CURRENT TRANSFORMER 400 1 SOLID RD 2.5ID | solid | round | 1 | 63 | 500 | PCSPCTFCL5001R | CURRENT TRANSFORMER 500 1 SPLIT Rect | Split | Rectangular |  | 1 | 69 | 168 | PCSPCT7RL1225 | CURRENT TRANSFORMER 1200 5 SOLID RD 2.5ID
[6 empty] | 500 | PCSPCT7RL5011 | CURRENT TRANSFORMER 500 1 SOLID RD 2.5ID | solid | round | 1 | 63 | 1000 | PCSPCTFCL10001R | CURRENT TRANSFORMER 1000 1 SPLIT Rect | Split | Rectangular |  | 1 | 69 | 168 | PCSPCT7RL1521 | CURRENT TRANSFORMER 1500 1 SOLID RD 2.5ID
Select CT according to current rating of: |  |  |  | Bus current rating: |  | 600 | PCSPCT7RL6011 | CURRENT TRANSFORMER 600 1 SOLID RD 2.5ID | solid | round | 1 | 63 | 1200 | PCSPCTFCL12001R | CURRENT TRANSFORMER 1200 1 SPLIT Rect | Split | Rectangular |  | 1 | 69 | 168 | PCSPCT7RL1525 | CURRENT TRANSFORMER 1500 5 SOLID RD 2.5ID
Are single phase loads present? |  |  | No |  |  | 750 | PCSPCT7RL7511 | CURRENT TRANSFORMER 750 1 SOLID RD 2.5ID | solid | round | 1 | 63 | 1500 | PCSPCTFCL15001R | CURRENT TRANSFORMER 1500 1 SPLIT Rect | Split | Rectangular |  | 1 | 69 | 168 | PCSPCT7RL1621 | CURRENT TRANSFORMER 1600 1 SOLID RD 2.5ID
| CT core construction: |  |  |  |  | 800 | PCSPCT7RL8011 | CURRENT TRANSFORMER 800 1 SOLID RD 2.5ID | solid | round | 1 | 63 | 1601 | PCSPCTFCL16001R | CURRENT TRANSFORMER 1600 1 SPLIT Rect | Split | Rectangular |  | 1 | 69 | 168 | PCSPCT7RL1625 | CURRENT TRANSFORMER 1600 5 SOLID RD 2.5ID
| CT mounted on: |  |  |  |  | 1000 | PCSPCT7RL1021 | CURRENT TRANSFORMER 1000 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL2011 | CURRENT TRANSFORMER 200 1 SOLID RD 2.5ID
| Secondary Current Rating: |  |  |  |  | 1200 | PCSPCT7RL1221 | CURRENT TRANSFORMER 1200 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL3011 | CURRENT TRANSFORMER 300 1 SOLID RD 2.5ID
[6 empty] | 1500 | PCSPCT7RL1521 | CURRENT TRANSFORMER 1500 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL3015 | CURRENT TRANSFORMER 300 5 SOLID RD 2.5ID
| CT Selecton |  |  |  |  | 1601 | PCSPCT7RL1621 | CURRENT TRANSFORMER 1600 1 SOLID RD 2.5ID | solid | round | 1 | 63 | [9 empty] | PCSPCT7RL4011 | CURRENT TRANSFORMER 400 1 SOLID RD 2.5ID
| Qty | Model Number | Description | [18 empty] | PCSPCT7RL4015 | CURRENT TRANSFORMER 400 5 SOLID RD 2.5ID
| 2 | [20 empty] | PCSPCT7RL5011 | CURRENT TRANSFORMER 500 1 SOLID RD 2.5ID
[6 empty] | 300 | PCSPCT7RL3015 | CURRENT TRANSFORMER 300 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 500 | PCSPCTFCL5005R | CURRENT TRANSFORMER 500 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL5015 | CURRENT TRANSFORMER 500 5 SOLID RD 2.5ID
[6 empty] | 400 | PCSPCT7RL4015 | CURRENT TRANSFORMER 400 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 1000 | PCSPCTFCL10005R | CURRENT TRANSFORMER 1000 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL6011 | CURRENT TRANSFORMER 600 1 SOLID RD 2.5ID
The above selection assumes one mains (power) source. If more mains (power) sources are present, then additional sets of CT may be required. One set per source location may be required. | [5 empty] | 500 | PCSPCT7RL5015 | CURRENT TRANSFORMER 500 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 1200 | PCSPCTFCL12005R | CURRENT TRANSFORMER 1200 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL6015 | CURRENT TRANSFORMER 600 5 SOLID RD 2.5ID
Selection of Current Transformers (CT) is site and load specific. The amperage rating of the CT primary must meet or exceed the expected maximum load current amplitude to be measured. | [5 empty] | 600 | PCSPCT7RL6015 | CURRENT TRANSFORMER 600 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 1500 | PCSPCTFCL15005R | CURRENT TRANSFORMER 1500 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL7511 | CURRENT TRANSFORMER 750 1 SOLID RD 2.5ID
CT used with AccuSine PCS+ and PFV+ may have 1 or 5 amp secondary. AccuSine PCS+ and AccuSine PFV+ have CT burdens of 1 VA for 5 amp secondaries and 0.04 VA for 1 amp secondaries. Be sure the CT have adequate VA rating. VA rating is based upon the quatity of AccuSine+ units connected in parallel, the CT secondary ampere rating, the total distance of the CT cable lengths, and the resistance (per meter) of the cable size selected. | [5 empty] | 750 | PCSPCT7RL7515 | CURRENT TRANSFORMER 750 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 1600 | PCSPCTFCL16005R | CURRENT TRANSFORMER 1600 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL7515 | CURRENT TRANSFORMER 750 5 SOLID RD 2.5ID
AccuSine PCS+ and AccuSine PFV+ may use CT with 50-60 Hz frequency response with Class 1 accuracy (Instrument rated). AccuSine PCS+ and AccuSine PFV+ require two CT per location. If single phase loads are present, then 3 CT per location are required. | [5 empty] | 800 | PCSPCT7RL8015 | CURRENT TRANSFORMER 800 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 2000 | PCSPCTFCL20005R | CURRENT TRANSFORMER 2000 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL8011 | CURRENT TRANSFORMER 800 1 SOLID RD 2.5ID
[6 empty] | 1000 | PCSPCT7RL1025 | CURRENT TRANSFORMER 1000 5 SOLID RD 2.5ID | solid | round | 5 | 63 | 3001 | PCSPCTFCL30005R | CURRENT TRANSFORMER 3000 5 SPLIT Rect | Split | Rectangular |  | 5 | 69 | 168 | PCSPCT7RL8015 | CURRENT TRANSFORMER 800 5 SOLID RD 2.5ID
If there are any questions, please, consult your Schneider Electric representative. | [5 empty] | 1200 | PCSPCT7RL1225 | CURRENT TRANSFORMER 1200 5 SOLID RD 2.5ID | solid | round | 5 | 63 | [9 empty] | PCSPCTFC1000058 | CURRENT TRANSFORMER 10000 5 SPLIT RND 8ID
[6 empty] | 1500 | PCSPCT7RL1525 | CURRENT TRANSFORMER 1500 5 SOLID RD 2.5ID | solid | round | 5 | 63 | [9 empty] | PCSPCTFC7500511 | CURRENT TRANSFORMER 7500 5 SPLIT RND 11ID
[6 empty] | 1601 | PCSPCT7RL1625 | CURRENT TRANSFORMER 1600 5 SOLID RD 2.5ID | solid | round | 5 | 63 | [9 empty] | PCSPCTFC750058 | CURRENT TRANSFORMER 7500 5 SPLIT RND 8ID
[22 empty] | PCSPCTFCL100014 | CURRENT TRANSFORMER 1000 1 SPLIT RND 4ID
[6 empty] | 500 | PCSPCTFCL50014 | CURRENT TRANSFORMER 500 1 SPLIT RND 4ID | Split | round | 1 | 101 | 2501 | PCSPCTFCL25001R411 | CURRENT TRANSFORMER 2500 1 SPLIT Rect 4X11 | Split | Rectangular |  | 1 | 101 | 279 | PCSPCTFCL100016 | CURRENT TRANSFORMER 1000 1 SPLIT RND 6ID
[6 empty] | 1001 | PCSPCTFCL100014 | CURRENT TRANSFORMER 1000 1 SPLIT RND 4ID | Split | round | 1 | 101 | [9 empty] | PCSPCTFCL10001R | CURRENT TRANSFORMER 1000 1 SPLIT Rect
[22 empty] | PCSPCTFCL100054 | CURRENT TRANSFORMER 1000 5 SPLIT RND 4ID
[6 empty] | 500 | PCSPCTFCL50016 | CURRENT TRANSFORMER 500 1 SPLIT RND 6ID | Split | round | 1 | 152 | [9 empty] | PCSPCTFCL10005R | CURRENT TRANSFORMER 1000 5 SPLIT Rect
[6 empty] | 1000 | PCSPCTFCL100016 | CURRENT TRANSFORMER 1000 1 SPLIT RND 6ID | Split | round | 1 | 152 | [9 empty] | PCSPCTFCL12001R | CURRENT TRANSFORMER 1200 1 SPLIT Rect
[6 empty] | 1500 | PCSPCTFCL150016 | CURRENT TRANSFORMER 1500 1 SPLIT RND 6ID | Split | round | 1 | 152 | [9 empty] | PCSPCTFCL120056 | CURRENT TRANSFORMER 1200 5 SPLIT RND 6ID
[6 empty] | 2001 | PCSPCTFCL200016 | CURRENT TRANSFORMER 2000 1 SPLIT RND 6ID | Split | round | 1 | 152 | [9 empty] | PCSPCTFCL12005R | CURRENT TRANSFORMER 1200 5 SPLIT Rect
[11 empty] | 1 | 152 | [9 empty] | PCSPCTFCL1500111 | CURRENT TRANSFORMER 1500 1 SPLIT RND 11ID
[13 empty] | 2500 | PCSPCTFCL25005R411 | CURRENT TRANSFORMER 2500 5 SPLIT Rect 4X11 | Split | Rectangular |  | 5 | 101 | 279 | PCSPCTFCL150016 | CURRENT TRANSFORMER 1500 1 SPLIT RND 6ID
[11 empty] | 1 | 203 | 3000 | PCSPCTFCL30005R411 | CURRENT TRANSFORMER 3000 5 SPLIT Rect 4X11 | Split | Rectangular |  | 5 | 101 | 279 | PCSPCTFCL150018 | CURRENT TRANSFORMER 1500 1 SPLIT RND 8ID
[6 empty] | 2000 | PCSPCTFCL200018 | CURRENT TRANSFORMER 2000 1 SPLIT RND 8ID | Split | round | 1 | 203 | 4000 | PCSPCTFCL40005R411 | CURRENT TRANSFORMER 4000 5 SPLIT Rect 4X11 | Split | Rectangular |  | 5 | 101 | 279 | PCSPCTFCL15001R | CURRENT TRANSFORMER 1500 1 SPLIT Rect
[6 empty] | 2501 | PCSPCTFCL250018 | CURRENT TRANSFORMER 2500 1 SPLIT RND 8ID | Split | round | 1 | 203 | 5001 | PCSPCTFCL50005R411 | CURRENT TRANSFORMER 5000 5 SPLIT Rect 4X11 | Split | Rectangular |  | 5 | 101 | 279 | PCSPCTFCL150054 | CURRENT TRANSFORMER 1500 5 SPLIT RND 4ID
[11 empty] | 1 | 203 | [9 empty] | PCSPCTFCL15005R | CURRENT TRANSFORMER 1500 5 SPLIT Rect
[22 empty] | PCSPCTFCL16001R | CURRENT TRANSFORMER 1600 1 SPLIT Rect
[6 empty] | 2501 | PCSPCTFCL2500111 | CURRENT TRANSFORMER 2500 1 SPLIT RND 11ID | Split | round | 1 | 279 | [9 empty] | PCSPCTFCL160054 | CURRENT TRANSFORMER 1600 5 SPLIT RND 4ID
[22 empty] | PCSPCTFCL16005R | CURRENT TRANSFORMER 1600 5 SPLIT Rect
[6 empty] | 500 | PCSPCTFCL50054 | CURRENT TRANSFORMER 500 5 SPLIT RND 4ID | Split | round | 5 | 101 | solid rd | [8 empty] | PCSPCTFCL200016 | CURRENT TRANSFORMER 2000 1 SPLIT RND 6ID
[6 empty] | 1000 | PCSPCTFCL100054 | CURRENT TRANSFORMER 1000 5 SPLIT RND 4ID | Split | round | 5 | 101 | split rd | FALSE | [7 empty] | PCSPCTFCL200018 | CURRENT TRANSFORMER 2000 1 SPLIT RND 8ID
[6 empty] | 1500 | PCSPCTFCL150054 | CURRENT TRANSFORMER 1500 5 SPLIT RND 4ID | Split | round | 5 | 101 | split rect | FALSE |  | Bus | Yes | Solid | Cable | 1 |  | PCSPCTFCL20001R | CURRENT TRANSFORMER 2000 1 SPLIT Rect
[6 empty] | 1601 | PCSPCTFCL160054 | CURRENT TRANSFORMER 1600 5 SPLIT RND 4ID | Split | round | 5 | 101 |  |  |  | Load | No | Split | Busbar | 5 |  | PCSPCTFCL200056 | CURRENT TRANSFORMER 2000 5 SPLIT RND 6ID
[22 empty] | PCSPCTFCL20005R | CURRENT TRANSFORMER 2000 5 SPLIT Rect
[6 empty] | 500 | PCSPCTFCL50056 | CURRENT TRANSFORMER 500 5 SPLIT RND 6ID | Split | round | 5 | 152 | [9 empty] | PCSPCTFCL250016 | CURRENT TRANSFORMER 2500 1 SPLIT RND 6ID
[6 empty] | 1200 | PCSPCTFCL120056 | CURRENT TRANSFORMER 1200 5 SPLIT RND 6ID | Split | round | 5 | 152 |  | Required Current Rating | [7 empty] | PCSPCTFCL25001R | CURRENT TRANSFORMER 2500 1 SPLIT Rect
[6 empty] | 2000 | PCSPCTFCL200056 | CURRENT TRANSFORMER 2000 5 SPLIT RND 6ID | Split | round | 5 | 152 |  | 0 | 501 | [6 empty] | PCSPCTFCL25001R411 | CURRENT TRANSFORMER 2500 1 SPLIT Rect 4X11
[6 empty] | 2500 | PCSPCTFCL250056 | CURRENT TRANSFORMER 2500 5 SPLIT RND 6ID | Split | round | 5 | 152 | [9 empty] | PCSPCTFCL2500511 | CURRENT TRANSFORMER 2500 5 SPLIT RND 11ID
[6 empty] | 3001 | PCSPCTFCL300056 | CURRENT TRANSFORMER 3000 5 SPLIT RND 6ID | Split | round | 5 | 152 | solid round 1A | [8 empty] | PCSPCTFCL250056 | CURRENT TRANSFORMER 2500 5 SPLIT RND 6ID
[13 empty] | solid round 5A | [8 empty] | PCSPCTFCL250058 | CURRENT TRANSFORMER 2500 5 SPLIT RND 8ID
[6 empty] | 2500 | PCSPCTFCL250058 | CURRENT TRANSFORMER 2500 5 SPLIT RND 8ID | Split | round | 5 | 203 | split round 1A 4" | [8 empty] | PCSPCTFCL25005R | CURRENT TRANSFORMER 2500 5 SPLIT Rect
[6 empty] | 4000 | PCSPCTFCL400058 | CURRENT TRANSFORMER 4000 5 SPLIT RND 8ID | Split | round | 5 | 203 | Split round 5A 4" | [8 empty] | PCSPCTFCL25005R411 | CURRENT TRANSFORMER 2500 5 SPLIT Rect 4X11
[6 empty] | 5001 | PCSPCTFCL500058 | CURRENT TRANSFORMER 5000 5 SPLIT RND 8ID | Split | round | 5 | 203 | split round 1A 6" | [8 empty] | PCSPCTFCL300016 | CURRENT TRANSFORMER 3000 1 SPLIT RND 6ID
[11 empty] | 5 | 203 | Split round 5A 6" | [8 empty] | PCSPCTFCL30001R | CURRENT TRANSFORMER 3000 1 SPLIT Rect
[11 empty] | 5 | 203.2 | split round 1A 8" | [8 empty] | PCSPCTFCL30001R411 | CURRENT TRANSFORMER 3000 1 SPLIT Rect 4X11
[13 empty] | Split round 5A 8" | PCSPCTFCL250058 | [7 empty] | PCSPCTFCL300056 | CURRENT TRANSFORMER 3000 5 SPLIT RND 6ID
[13 empty] | split round 1A 11" | [8 empty] | PCSPCTFCL30005R | CURRENT TRANSFORMER 3000 5 SPLIT Rect
[6 empty] | 2501 | PCSPCTFCL2500511 | CURRENT TRANSFORMER 2500 5 SPLIT RND 11ID | Split | round | 5 | 279 | Split round 5A 11" | [8 empty] | PCSPCTFCL30005R411 | CURRENT TRANSFORMER 3000 5 SPLIT Rect 4X11
[11 empty] | 5 | 279 | [9 empty] | PCSPCTFCL400018 | CURRENT TRANSFORMER 4000 1 SPLIT RND 8ID
[13 empty] | rect small 1A | [8 empty] | PCSPCTFCL40001R411 | CURRENT TRANSFORMER 4000 1 SPLIT Rect 4X11
[13 empty] | rect small 5A | [8 empty] | PCSPCTFCL400058 | CURRENT TRANSFORMER 4000 5 SPLIT RND 8ID
[13 empty] | Rect Large 1A | [8 empty] | PCSPCTFCL40005R411 | CURRENT TRANSFORMER 4000 5 SPLIT Rect 4X11
[13 empty] | Rect large 5A | [8 empty] | PCSPCTFCL500018 | CURRENT TRANSFORMER 5000 1 SPLIT RND 8ID
[22 empty] | PCSPCTFCL50001R411 | CURRENT TRANSFORMER 5000 1 SPLIT Rect 4X11
[22 empty] | PCSPCTFCL500058 | CURRENT TRANSFORMER 5000 5 SPLIT RND 8ID
[22 empty] | PCSPCTFCL50005R411 | CURRENT TRANSFORMER 5000 5 SPLIT Rect 4X11
[22 empty] | PCSPCTFCL50014 | CURRENT TRANSFORMER 500 1 SPLIT RND 4ID
[12 empty] | Solid | [9 empty] | PCSPCTFCL5001R | CURRENT TRANSFORMER 500 1 SPLIT Rect
[12 empty] | Split 1 | [9 empty] | PCSPCTFCL50054 | CURRENT TRANSFORMER 500 5 SPLIT RND 4ID
[12 empty] | Split 5 | [9 empty] | PCSPCTFCL50056 | CURRENT TRANSFORMER 500 5 SPLIT RND 6ID
[12 empty] | Rect SM 1 | [9 empty] | PCSPCTFCL5005R | CURRENT TRANSFORMER 500 5 SPLIT Rect
Rect SM 5
Rect 411 1
Rect 411 5
Comment for d17

## Typical THDi levels
% THDi at full load levels based upon installed inductive impedance and source to load short circuit ratio (ShCR)
Typical THDi Levels
| AVG Impedance (Z%) | ShCR = 20 | ShCR = 50 | ShCR = 100 | ShCR = 150 | ShCR = 250 | ShCR = 500 | ShCR = 1000 | ShCR = 2500
|  | 20 | 50 | 100 | 150 | 250 | 500 | 1000 | 2500
| 0% | 26.44% | 56.31% | 75.36% | 91.9% | 113.6% | 123.2% | 139.1% | 184.8%
| 1.123% | 21.83% | 38.8% | 48.82% | 54.23% | 57.69% | 60.62% | 62.35% | 63.72%
| 1.5% | 20.5% | 35.31% | 42.23% | 46.36% | 49.37% | 50.11% | 50.88% | 51.73%
| 2.614% | 17.82% | 27.85% | 32.93% | 35.44% | 37.08% | 38.45% | 39.24% | 39.36%
| 3% | 16.82% | 25.38% | 29.18% | 31.17% | 33.16% | 33.14% | 33.59% | 33.97%
| 4.222% | 15.08% | 21.55% | 24.52% | 25.92% | 26.79% | 27.53% | 27.95% | 28.03%
| 5% | 13.58% | 18.92% | 20.82% | 21.82% | 22.5% | 22.66% | 22.81% | 22.99%
| 5.972% | 13% | 16.55% | 19.11% | 20.08% | 20.61% | 21.05% | 21.3% | 21.33%
| 7.5% | 11.59% | 14.6% | 15.78% | 16.37% | 16.73% | 16.91% | 17.02% | 17.12%